{"text_format":"2","workbook":"xlsx","n_sheets":2,"sheets":["NTP02 Heater Sheet","Sheet1"],"not_rendered":{"charts":0,"images":2,"macros":0,"external_links":0,"defined_names":1,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900"}

{"sheet":"NTP02 Heater Sheet","index":0,"n_rows":92,"n_cols":22,"rows_kept":92,"cut":false,"hidden":false,"merged":[[1,19,1,20],[2,1,2,4],[2,5,2,16],[3,1,3,4],[3,5,3,12],[4,6,4,8],[4,9,4,12],[88,3,88,20],[89,3,89,20],[90,3,90,20],[91,3,91,20],[4,0,5,0],[6,0,21,0],[22,0,37,0],[38,0,53,0],[54,0,69,0],[71,0,86,0],[4,1,5,1],[6,1,21,1],[22,1,37,1],[38,1,53,1],[54,1,69,1],[71,1,86,1],[4,2,5,2],[4,3,5,3],[4,4,5,4],[4,5,5,5],[4,13,5,13],[4,14,5,14],[4,15,5,15],[4,16,5,16],[2,19,3,19],[2,20,3,20],[0,2,1,12],[88,0,89,1]]}
[null,null,"Gas Line Heater(NTP02)"]
[{"$nulls":18},"Doc No.:","200-0020-000"]
["Design:","CH",null,null,null,"Design Change Description",{"$nulls":13},"Version:","E03"]
["Time:",20250311,{"$nulls":12},"Date:","Sig:","Appd:"]
["INI8 NO.","SW NO.","CH","Act","HEAT NO.","TC NO.","Memory1",null,null,"Memory2",null,null,null,"PN","Description","QTY","CONNECTION","VOLTAGE","POWER MAX","Current","FUSE"]
[{"$nulls":6},"SET","LO-TMP","HI-TMP","SV","LO-TMP","HI-TMP","CLN.T",{"$nulls":4},"V","W","A","A"]
["MINI8-1","HTR1","U1-CH1","DCS  GAS IN","H101","TC101","40℃","30℃","60℃","40℃","30℃","60℃","60℃","539-2051-000","20×500mm",1,null,220,{"$f":"0.5*150","v":75},{"$f":"S7/R7","v":0.340909090909091},0.5]
[null,null,"U1-CH2","IGS 1","H102","TC102","40℃","30℃","60℃","40℃","30℃","60℃","60℃","tube1-10","20×400mm",1,null,220,{"$f":"0.4*150","v":60},{"$f":"S8/R8","v":0.272727272727273},0.5]
[null,null,"U1-CH3","IGS 2","H103","TC103","40℃","30℃","60℃","40℃","30℃","60℃","60℃","tube1-5","20×500mm",1,null,220,75,{"$f":"S9/R9","v":0.340909090909091},0.5]
[null,null,"U1-CH4","IGS 3","H104","TC104","40℃","30℃","60℃","40℃","30℃","60℃","60℃","tube1-6","20×400mm",1,null,220,{"$f":"0.4*150","v":60},{"$f":"S10/R10","v":0.272727272727273},0.5]
[null,null,"U1-CH5","IGS 4","H105","TC105","40℃","30℃","60℃","40℃","30℃","60℃","60℃",null,"SELF-HEATING",1,null,220,40,0.182,0.25]
[null,null,"U1-CH6","IGS 5","H106","TC106","40℃","30℃","60℃","40℃","30℃","60℃","60℃",null,"SELF-HEATING",1,null,220,30,0.136,0.25]
[null,null,"U1-CH7","REC-1-1","H107","TC107","40℃","30℃","60℃","40℃","30℃","60℃","60℃","539-2043-000","20×750mm",1,null,220,{"$f":"0.75*150","v":112.5},{"$f":"S13/R13","v":0.511363636363636},1]
[null,null,"U1-CH8","REC-4-1-1","H108","TC108","40℃","30℃","60℃","40℃","30℃","60℃","60℃","539-2042-000","20×900mm",1,null,220,{"$f":"0.9*150","v":135},{"$f":"S14/R14","v":0.613636363636364},1]
[null,null,"U1-CH9","REC-4-1-2","H109","TC109","40℃","30℃","60℃","40℃","30℃","60℃","60℃","539-2077-000","20×2000mm",1,null,220,{"$f":"2*150","v":300},{"$f":"S15/R15","v":1.36363636363636},2]
[null,null,"U1-CH10","REC-1-2","H110","TC110","120℃","100℃","140℃","40℃","30℃","140℃","120℃","539-2066-000","20×400mm",1,null,220,{"$f":"0.4*150","v":60},{"$f":"S16/R16","v":0.272727272727273},0.5]
[null,null,"U1-CH11","REC-4-2","H111","TC111","120℃","100℃","140℃","40℃","30℃","140℃","120℃","539-2066-000","20×400mm",1,null,220,{"$f":"0.4*150","v":60},{"$f":"S17/R17","v":0.272727272727273},0.5]
[null,null,"U1-CH12","AV28","H112","TC112","120℃","100℃","140℃","40℃","30℃","140℃","120℃",null,"JK-HEATER",1,null,220,{"$f":"R18*T18","v":61.6},0.28,0.5]
[null,null,"U1-CH13","AV29","H113","TC113","120℃","100℃","140℃","40℃","30℃","140℃","120℃",null,"JK-HEATER",1,null,220,{"$f":"R19*T19","v":61.6},0.28,0.5]
[null,null,"U1-CH14"]
[null,null,"U1-CH15"]
[null,null,"U1-CH16"]
["MINI8-2","HTR1","U2-CH1","AV30","H201","TC201","120℃","100℃","140℃","40℃","30℃","140℃","120℃",null,"JK-HEATER",1,null,220,{"$f":"R23*T23","v":61.6},0.28,0.5]
[null,null,"U2-CH2","AV31","H202","TC202","120℃","100℃","140℃","40℃","30℃","140℃","120℃",null,"JK-HEATER",1,null,220,{"$f":"R24*T24","v":61.6},0.28,0.5]
[null,null,"U2-CH3","DCS-TANK1","H203","TC203","120℃","100℃","140℃","60℃","40℃","140℃","120℃",null,"JK-HEATER",1,null,220,{"$f":"R25*T25","v":129.796991069752},{"$f":"R25/372.89","v":0.589986323044329},1]
[null,null,"U2-CH4","DCS-TANK2","H204","TC204","120℃","100℃","140℃","60℃","40℃","140℃","120℃",null,"JK-HEATER",1,null,220,{"$f":"R26*T26","v":129.796991069752},{"$f":"R26/372.89","v":0.589986323044329},2]
[null,null,"U2-CH5","AV32-33","H205","TC205","120℃","100℃","140℃","60℃","40℃","140℃","120℃",null,"JK-HEATER",1,null,220,{"$f":"R27*T27","v":50.6},0.23,0.25]
[null,null,"U2-CH6","AV34-35","H206","TC206","120℃","100℃","140℃","60℃","40℃","140℃","120℃",null,"JK-HEATER",1,null,220,50.6,0.23,0.25]
[null,null,"U2-CH7","AV36","H207","TC207","120℃","100℃","140℃","60℃","40℃","140℃","120℃",null,"JK-HEATER",1,null,220,61.6,0.28,0.5]
[null,null,"U2-CH8","AV37","H208","TC208","120℃","100℃","140℃","60℃","40℃","140℃","120℃",null,"JK-HEATER",1,null,220,61.6,0.28,0.5]
[null,null,"U2-CH9","AV38","H209","TC209","120℃","100℃","140℃","60℃","40℃","140℃","120℃",null,"JK-HEATER",1,null,220,61.6,0.28,0.5]
[null,null,"U2-CH10","AV39","H210","TC210","120℃","100℃","140℃","60℃","40℃","140℃","120℃",null,"JK-HEATER",1,null,220,61.6,0.28,0.5]
[null,null,"U2-CH11","AV52","H211","TC211","120℃","100℃","140℃","60℃","40℃","140℃","120℃",null,"JK-HEATER",1,null,220,61.6,0.28,0.5]
[null,null,"U2-CH12","REC-1-1-1","H212","TC212","40℃","30℃","60℃","40℃","30℃","60℃","60℃","539-2076-000","20×1400mm",1,null,220,{"$f":"1.4*150","v":210},{"$f":"S34/R34","v":0.954545454545455},1]
[null,null,"U2-CH13"]
[null,null,"U2-CH14"]
[null,null,"U2-CH15"]
[null,null,"U2-CH16"]
["MINI8-3","HTR1","U3-CH1","REC-1-3","H301","TC301","150℃","130℃","170℃","60℃","40℃","140℃","120℃","539-2067-000","20×1300mm",1,null,220,{"$f":"1.3*150","v":195},{"$f":"S39/R39","v":0.886363636363636},1]
[null,null,"U3-CH2","REC-4-3","H302","TC302","150℃","130℃","170℃","60℃","40℃","140℃","120℃","539-2068-000","20×1400mm",1,null,220,210,{"$f":"S40/R40","v":0.954545454545455},1]
[null,null,"U3-CH3","REC-1-4","H303","TC303","150℃","130℃","170℃","60℃","40℃","140℃","120℃","539-2086-000","20×1400mm",1,null,220,210,{"$f":"S41/R41","v":0.954545454545455},1]
[null,null,"U3-CH4","REC-4-4","H304","TC304","150℃","130℃","170℃","60℃","40℃","140℃","120℃","539-2092-000","20×1100mm",1,null,220,{"$f":"1.1*150","v":165},0.75,1]
[null,null,"U3-CH5","N2 OUT-1-1","H305","TC305","150℃","130℃","170℃","60℃","40℃","140℃","120℃","539-2072-000","20×1600mm",1,null,220,{"$f":"150*1.6","v":240},1.09090909090909,2]
[null,null,"U3-CH6","N2 OUT-1-2","H306","TC306","150℃","130℃","170℃","60℃","40℃","140℃","120℃","539-2091-000","20×750mm",1,null,220,{"$f":"0.75*150","v":112.5},0.511363636363636,1]
[null,null,"U3-CH7","REC-2-1","H307","TC307","180℃","160℃","200℃","60℃","40℃","200℃","120℃","539-2070-000","20×1200mm",1,null,220,{"$f":"1.2*150","v":180},0.818181818181818,1]
[null,null,"U3-CH8","REC-2-2","H308","TC308","180℃","160℃","200℃","60℃","40℃","200℃","120℃","539-2085-000","20×500mm",1,null,220,{"$f":"0.5*150","v":75},0.340909090909091,0.5]
[null,null,"U3-CH9","REC-2-2-1","H309","TC309","180℃","160℃","200℃","60℃","40℃","200℃","120℃","539-2112-000","20×400mm",1,null,220,{"$f":"0.4*150","v":60},0.272727272727273,0.5]
[null,null,"U3-CH10","REC-3-1","H310","TC310","180℃","160℃","200℃","60℃","40℃","200℃","120℃","539-2071-000","20×1300mm",1,null,220,{"$f":"1.3*150","v":195},0.886363636363636,1]
[null,null,"U3-CH11","REC-3-2","H311","TC311","180℃","160℃","200℃","60℃","40℃","200℃","120℃","539-2093-000","20×950mm",1,null,220,{"$f":"0.95*150","v":142.5},0.647727272727273,1]
[null,null,"U3-CH12","REC-3-2-1","H312","TC312","180℃","160℃","200℃","60℃","40℃","200℃","120℃","539-2112-000","20×400mm",1,null,220,{"$f":"0.4*150","v":60},0.272727272727273,0.5]
[null,null,"U3-CH13","SEAL CAP","H313","TC313","150℃","130℃","250℃","100℃","80℃","250℃","200℃",null,null,1,null,220,700,3.18181818181818,4]
[null,null,"U3-CH14","R AXIS",null,"TC314","80℃","30℃","110℃","30℃","30℃","110℃","70℃",null,null,1,null,"无加热","TC监测"]
[null,null,"U3-CH15"]
[null,null,"U3-CH16"]
["MINI8-4","HTR2","U4-CH1","APC RING(CKD VALVE)","H401","TC401","190℃","170℃","200℃","100℃","80℃","200℃","120℃",null,"SELF-HEATING",1,null,100,85,{"$f":"S55/R55","v":0.85},1]
[null,null,"U4-CH2","APC OUT(CKD VALVE)","H402","TC402","190℃","170℃","200℃","100℃","80℃","200℃","120℃",null,"SELF-HEATING",1,null,100,315,3.15,4]
[null,null,"U4-CH3","INLET HEATER-1","H403","TC403","150℃","130℃","300℃","0℃","0℃","300℃","180℃",null,null,1,"串联",100,455,4.55,5,"4个串联"]
[null,null,"U4-CH4","INLET HEATER-2","H404","TC404","150℃","130℃","300℃","0℃","0℃","300℃","180℃",null,null,1,"串联",100,470,4.7,5,"2个串联"]
[null,null,"U4-CH5","INLET PORT HEATER-1","H405-1,2,3","TC405","150℃","130℃","300℃","0℃","0℃","300℃","180℃",null,null,1,"串联",100,130,1.3,2,"3个串联"]
[null,null,"U4-CH6","INLET PORT HEATER-2","H406-1,2,3","TC406","150℃","130℃","300℃","0℃","0℃","300℃","180℃",null,null,1,"串联",100,108,1.08,2,"3个串联"]
[null,null,"U4-CH7","TUBE PORT","H407","TC407","180℃","160℃","230℃","0℃","0℃","230℃","120℃",null,null,1,null,220,30,0.136363636363636,0.25]
[null,null,"U4-CH8","JACKET HEATER-1","H408","TC408","180℃","160℃","200℃","0℃","0℃","200℃","120℃",null,"JK-HEATER",1,null,220,475,2.15909090909091,3.15]
[null,null,"U4-CH9","JACKET HEATER-2","H409","TC409","180℃","160℃","210℃","0℃","0℃","210℃","120℃",null,"JK-HEATER",1,null,220,115,0.522727272727273,1]
[null,null,"U4-CH10","JACKET HEATER-3","H410","TC410","180℃","160℃","200℃","0℃","0℃","200℃","120℃",null,"JK-HEATER",1,null,220,471,2.14090909090909,3.15]
[null,null,"U4-CH11","JACKET HEATER-4","H411","TC411","180℃","160℃","200℃","0℃","0℃","200℃","120℃",null,"JK-HEATER",1,null,220,494,2.24545454545455,3.15]
[null,null,"U4-CH12","JACKET HEATER-5","H412","TC412","180℃","160℃","200℃","0℃","0℃","200℃","120℃",null,"JK-HEATER",1,null,220,50,0.227272727272727,0.25]
[null,null,"U4-CH13","JACKET HEATER-6","H413","TC413","180℃","160℃","200℃","0℃","0℃","200℃","120℃",null,"JK-HEATER",1,null,220,206,{"$f":"S67/R67","v":0.936363636363636},1]
[null,null,"U4-CH14","JACKET HEATER-7","H414","TC414","180℃","160℃","200℃","0℃","0℃","200℃","120℃",null,"JK-HEATER",1,null,220,38,0.172727272727273,0.25]
[null,null,"U4-CH15"]
[null,null,"U4-CH16"]
["MINI8-5","炉子"]
["MINI8-6","HTR2","U6-CH1","JACKET HEATER-8","H601","TC601","180℃","160℃","200℃","0℃","0℃","200℃","120℃",null,"JK-HEATER",1,null,220,50,0.227272727272727,0.25]
[null,null,"U6-CH2","JACKET HEATER-9","H602","TC602","180℃","160℃","200℃","0℃","0℃","200℃","120℃",null,"JK-HEATER",1,null,220,37,0.168181818181818,0.25]
[null,null,"U6-CH3","JACKET HEATER-10","H603","TC603","180℃","160℃","200℃","0℃","0℃","200℃","120℃",null,"JK-HEATER",1,null,220,42,0.190909090909091,0.25]
[null,null,"U6-CH4","JACKET HEATER-11","H604","TC604","180℃","160℃","200℃","0℃","0℃","200℃","120℃",null,"JK-HEATER",1,null,220,55,{"$f":"S75/R75","v":0.25},0.5]
[null,null,"U6-CH5","JACKET HEATER-12","H605","TC605","180℃","160℃","200℃","0℃","0℃","200℃","120℃",null,"JK-HEATER",1,null,220,82,0.372727272727273,0.5]
[null,null,"U6-CH6","JACKET HEATER-13","H606","TC606","180℃","160℃","200℃","0℃","0℃","200℃","120℃",null,"JK-HEATER",1,null,220,88,0.4,0.5]
[null,null,"U6-CH7","JACKET HEATER-14","H607","TC607","180℃","160℃","200℃","0℃","0℃","200℃","120℃",null,"JK-HEATER",1,null,220,107.8,0.49,0.5]
[null,null,"U6-CH8","JACKET HEATER-15","H608","TC608","180℃","160℃","200℃","0℃","0℃","200℃","120℃",null,"JK-HEATER",1,null,220,93,0.422727272727273,0.5]
[null,null,"U6-CH9","JACKET HEATER-16","H609","TC609","180℃","160℃","200℃","0℃","0℃","200℃","120℃",null,"JK-HEATER",1,null,220,93,0.422727272727273,0.5]
[null,null,"U6-CH10","JACKET HEATER-17","H610","TC610","180℃","160℃","200℃","0℃","0℃","200℃","120℃",null,"JK-HEATER",1,null,220,93,0.422727272727273,0.5]
[null,null,"U6-CH11","JACKET HEATER-18","H611","TC611","180℃","160℃","200℃","0℃","0℃","200℃","120℃",null,"JK-HEATER",1,null,220,100,{"$f":"S82/R82","v":0.454545454545455},0.5]
[null,null,"U6-CH12","JACKET HEATER-19","H612","TC612","180℃","160℃","200℃","0℃","0℃","200℃","120℃",null,"JK-HEATER",1,null,220,50,0.227272727272727,0.25]
[null,null,"U6-CH13","JACKET HEATER-20","H613","TC613","180℃","160℃","200℃","0℃","0℃","200℃","120℃",null,"JK-HEATER",1,null,220,64,0.290909090909091,0.5]
[null,null,"U6-CH14","EXHAUST‑2","H614","TC614","180℃","160℃","200℃","0℃","0℃","200℃","120℃","539-2022-000","20×1600mm",1,null,220,{"$f":"1.6*150","v":240},1.09090909090909,2]
[null,null,"U6-CH15"]
[null,null,"U6-CH16"]
[]
["修改记录：",null,3.31,"电流电阻丝数据"]
[null,null,4.1,"1.MINI8-4点位变动"]
[null,null,null,"2.原MINI8-5改为炉子、新增MINI8-6为原MINI8-5"]
[null,null,null,"3.功率估值（仿照TIN Pro(管道)+ELK（铝块））"]

{"sheet":"Sheet1","index":1,"n_rows":15,"n_cols":16,"rows_kept":15,"cut":false,"hidden":false,"merged":[[13,4,13,8],[14,3,14,9],[0,3,1,3],[2,4,12,4],[2,6,12,6],[2,7,12,7],[2,8,12,8],[15,3,26,9]]}
["功率密度ρ",null,null,"PN","宽度B","加热带长度L","引线长度l","供电电压V","每米功率","数量",null,null,"米功率","电阻","数量","功率"]
["W/cm2",null,null,null,"mm","mm","mm","V","W/m","n",null,null,"W/m","Ω","n","W"]
[0.5,null,null,1,20,400,1500,110,75,null,null,null,{"$f":"ROUND(P3/(300-50)*1000,0)","v":104},{"$f":"ROUND($H$3^2/P3,0)","v":465},null,{"$f":"ROUND((F3-50)*9.52*3.14/100*$A$3/2,0)","v":26}]
[null,null,null,2,null,500,{"$nulls":6},{"$f":"ROUND(P4/(500-50)*1000,0)","v":76},{"$f":"ROUND($H$3^2/P4,0)","v":356},null,{"$f":"ROUND((F4-50)*9.52*3.14/100*$A$3/2,0)","v":34}]
[null,null,null,3,null,750,{"$nulls":6},{"$f":"ROUND(P5/(600-50)*1000,0)","v":95},{"$f":"ROUND($H$3^2/P5,0)","v":233},null,{"$f":"ROUND((F5-50)*9.52*3.14/100*$A$3/2,0)","v":52}]
[null,null,null,4,null,900,{"$nulls":6},{"$f":"ROUND(P6/(750-50)*1000,0)","v":91},{"$f":"ROUND($H$3^2/P6,0)","v":189},null,{"$f":"ROUND((F6-50)*9.52*3.14/100*$A$3/2,0)","v":64}]
[null,null,null,5,null,950,{"$nulls":6},{"$f":"ROUND(P7/(950-50)*1000,0)","v":74},{"$f":"ROUND($H$3^2/P7,0)","v":181},null,{"$f":"ROUND((F7-50)*9.52*3.14/100*$A$3/2,0)","v":67}]
[null,null,null,6,null,1100,{"$nulls":6},{"$f":"ROUND(P8/(1100-50)*1000,0)","v":74},{"$f":"ROUND($H$3^2/P8,0)","v":155},null,{"$f":"ROUND((F8-50)*9.52*3.14/100*$A$3/2,0)","v":78}]
[null,null,null,7,null,1200,{"$nulls":6},{"$f":"ROUND(P9/(1300-50)*1000,0)","v":69},{"$f":"ROUND($H$3^2/P9,0)","v":141},null,{"$f":"ROUND((F9-50)*9.52*3.14/100*$A$3/2,0)","v":86}]
[null,null,null,8,null,1300,{"$nulls":6},{"$f":"ROUND(P10/(1600-50)*1000,0)","v":60},{"$f":"ROUND($H$3^2/P10,0)","v":130},null,{"$f":"ROUND((F10-50)*9.52*3.14/100*$A$3/2,0)","v":93}]
[null,null,null,9,null,1400,{"$nulls":6},{"$f":"ROUND(P11/(2000-50)*1000,0)","v":52},{"$f":"ROUND($H$3^2/P11,0)","v":120},null,{"$f":"ROUND((F11-50)*9.52*3.14/100*$A$3/2,0)","v":101}]
[null,null,null,10,null,1600,{"$nulls":6},{"$f":"ROUND(P12/(2000-50)*1000,0)","v":59},{"$f":"ROUND($H$3^2/P12,0)","v":104},null,{"$f":"ROUND((F12-50)*9.52*3.14/100*$A$3/2,0)","v":116}]
[null,null,null,11,null,2000,{"$nulls":6},{"$f":"ROUND(P13/(2000-50)*1000,0)","v":75},{"$f":"ROUND($H$3^2/P13,0)","v":83},null,{"$f":"ROUND((F13-50)*9.52*3.14/100*$A$3/2,0)","v":146}]
[null,null,null,"合计"]
[null,null,null,"示意图"]